## Sheet1
ISA Tag | IO Description | IO Type | Units | Display | PCS Alarm | Special Notes
FN-01 | SPMP-01 - Discharge Flow Rate | AI | gpm | Y | Y | Alarm when 4-20mA signal is out of range | AI Count | 4
FN-02 | SPMP-02 - Discharge Flow Rate | AI | gpm | Y | Y | Alarm when 4-20mA signal is out of range | AO Count | 0
PN-01 | Station - Discharge Pressure | AI | PSI | Y | Y | Alarm when 4-20mA signal is out of range | DI Count | 30
LN-02 | Wet Well - Radar Level | AI |  | Y |  | Alarm when out of range, high-high level, and low low level | DO Count | 4
HNA-01 | SPMP-01 - HOA in Auto | DI |  | Y | Y | Alarm when false |  | HO
MNF-01 | SPMP-01 - Fault | DI |  | Y | Y
TNH-01 | SPMP-01 - High Temp | DI |  | Y | Y
LNH-01 | SPMP-01 - Seal Leak | DI |  | Y | Y
MNR-01 | SPMP-01 - Run Status | DI |  | Y
JNN-01 | SPMP-01 - Power Consumption KW Pulse | DI | KW | Y
HNA-02 | SPMP-02 - HOA in Auto | DI |  | Y | Y | Alarm when false
MNF-02 | SPMP-02 - Fault | DI |  | Y | Y
TNH-02 | SPMP-02 - High Temp | DI |  | Y | Y
LNH-02 | SPMP-02 - Seal Leak | DI |  | Y | Y
MNR-02 | SPMP-02 - Run Status | DI |  | Y
JNN-02 | SPMP-02 - Power Consumption KW Pulse | DI | KW | Y
QNA-01 | Secondary Control Panel - Secondary Control Active | DI |  | Y | Y
LNLL-01 | Secondary Control Panel - Low-Low Level Alarm | DI |  | Y | Y | Show if Sec Control Active
LNHH-01 | Secondary Control Panel - High-High Level Alarm | DI |  | Y | Y | Show if Sec Control Active
QNA-02 | Secondary Control Panel - Pump Down Failure | DI |  | Y | Y
LNL-01 | Secondary Control Panel - Low Level Alarm | DI |  | Y |  | Show if Sec Control Active
LNH-03 | Secondary Control Panel - High Level Alarm | DI |  | Y |  | Show if Sec Control Active
MNR-03 | Standby Diesel Bypass Pump - Run Status | DI |  | Y | Y
MNF-03 | Standby Diesel Bypass Pump - Fault | DI |  | Y | Y
LNL-01 | Standby Diesel Bypass Pump - Low Fuel | DI |  | Y | Y
HNQ-01 | Standby Diesel Bypass Pump - Not in Auto | DI |  | Y | Y
TNL-02 | Valve Enclosure - Pipe Freeze Possible | DI |  | Y | Y
JN-01 | PLC/RTU Panel - Control Power | DI |  |  | Y | Alarm when false
QP-01 | PLC/RTU Panel - Alarm Test | DI |  |  |  | Display at SCADA
ZN-01 | PLC/RTU Panel - Panel Intrusion | DI |  |  | Y
JNF-02 | PLC/RTU Panel - PS 1 Fault | DI |  |  | Y
JNF-03 | PLC/ RTU Panel - PS 2 Fault | DI |  |  | Y
JN-02 | UPS Control Panel - UPS on Battery | DI |  | Y | Y
JNF-01 | UPS Control Panel - UPS Fault | DI |  |  | Y
MCN-01 | SPMP-01 - Run CMD | DO |  | Y
MIR-01 | SPMP-01 - Bypass Pump Running | DO |  | Y
MCN-02 | SPMP-02 - Run CMD | DO |  | Y
MIR-02 | SPMP-02 - Bypass Pump Running | DO |  | Y
TNR-01 | Heat Tracing Controller - Heater On | TCP |  | Y
TNF-01 | Heat Tracing Controller - Heater Fault | TCP |  | Y | Y
TNL-01 | Heat Tracing Controller - Pipe Temperature | TCP | °F |  | Y | Alarm when below 40°F